## Scott Schedule
Brampton Leisure Limited v Hartwell Construction Ltd — Claim No. HT-2025-000219
SCOTT SCHEDULE OF DEFECTS (composite — Claimant's case, Defendant's response, Claimant's reply)
Prepared by Whitfield Carter LLP for the Claimant. Defendant entries reproduced from Defence and disclosure. £ exclusive of VAT.
Item | Element / Location | Defect alleged (Claimant) | Contract / standard breached | Claimant remedial cost (£) | Defendant's response | Defendant's valuation (£) | Claimant's reply
1.1 | Pool hall — curtain-wall / roof abutment | Inadequately designed and defectively installed abutment detail permitting persistent water ingress; corrosion of structural steelwork; partial poolside closure. | Cl. 2.1, 2.17; ER Section A2; CWCT Standard | 512000 | Constructed to Claimant's façade consultant's design; ingress due to lack of maintenance of rainwater goods. | 0 | Design was Contractor's Designed Portion; LFA report confirms workmanship failure at seals.
1.2 | Pool hall roof — steelwork corrosion | Corrosion to exposed steelwork arising from ingress; protective treatment and partial replacement required. | Cl. 2.1; BS EN ISO 12944 | 230500 | Denied; consequential on 1.1 which is denied. | 0 | Quantum supported by structural engineer's costing at NR1/166.
2.1 | Pool water-treatment plant — filtration | Filtration plant undersized against ER turnover rate; unable to maintain water quality. | Cl. 2.17; ER Section M3; PWTAG 2017 | 268000 | Plant sized to ER turnover figures provided by Employer; breaches due to over-occupancy. | 42000 | ER M3 turnover unambiguous; over-occupancy not made out on attendance data.
2.2 | Pool water-treatment plant — dosing/controls | Dosing system incorrectly commissioned; repeated combined-chlorine and pH excursions; 3 closures. | Cl. 2.1; ER M3; PWTAG | 150000 | Commissioning complete and signed off; operational mismanagement by Claimant. | 18000 | Commissioning records incomplete; EHO directions evidence underlying plant inadequacy.
3.1 | Pool hall ventilation — AHUs | Air-handling units undersized; cannot maintain design humidity; condensation and mould. | Cl. 2.17; ER M4; CIBSE TM58 | 421400 | AHUs met design humidity at design water/air temperatures; Claimant ran outside design basis. | 65000 | Pool operated within CIBSE design basis; LFA airflow tests show shortfall of 22%.
3.2 | Pool hall finishes — mould remediation | Deterioration of finishes from condensation; strip-out and replacement of affected finishes. | Cl. 2.1 | 111000 | Denied; consequential on 3.1 which is denied. | 0 | Quantum agreed in principle subject to liability.
4.1 | Studios 2 & 3 — HVAC controls | Controls defectively installed; studios unusable summer 2024. | Cl. 2.1 | 64000 | No defect admitted; commissioning matter remediable in Rectification Period. | 12000 | Not notifiable as latent; defect outside Contractor's own commissioning sign-off.
TOTAL REMEDIAL WORKS
Note: Scott Schedule remedial total (£1,756,900) ties to the cost-of-works element of the Schedule of Loss. Loss of profit, professional fees and member compensation are pleaded separately in the Schedule of Loss.